## Fire Inspection Report
Housing Projects Managed by HRDE—Fire Alarm/Range Hood/Sprinkler/Extinguisher/ Backflow Preventer/ Fire Suppression Inspections
Quarterly: • Sprinklers are to be inspected by a certified technician quarterly/four (4) times per year. • Additional Inspection: Sprinklers are to be drained by a certified technician once (1) per year. • Additional Inspection: Sprinkler gauges are to be changed by a certified technician every five (5) years. This process will include calibration of the gauges. It is a very good practice for a manager to use a permanent black marker and write the install date of the gauge on the gauge. • Additional Inspection: Sprinklers are to be inspected by a certified technician every five (5) years by opening a flushing connection at the end of one main and by removing a sprinkler head toward the end of one branch line to inspect for the presence of any foreign material. If any foreign material is present, an obstruction investigation shall be conducted. An obstruction investigation shall be conducted by a certified technician for system or yard main piping wherever any of the following conditions exist: (1) Defective intake for fire pumps taking suction from open bodies of water (2) The discharge of obstructive material during routine water tests (3) Foreign materials in fire pumps, in dry pipe valves, or in check valves (4) Foreign material in water during drain tests or plugging of inspector’s test connection(s) (5) Plugged sprinklers (6) Plugged piping in sprinkler systems dismantled during building alterations (7) Failure to flush yard piping or surrounding public mains following new installations or repairs (8) A record of broken public mains in the vicinity (9) Abnormally frequent false tripping of a dry pipe valve(s) (10) A system that is returned to service after an extended shutdown (greater than 1 year) (11) There is reason to believe that the sprinkler system contains sodium silicate or highly corrosive fluxes in copper systems (12) A system has been supplied with raw water via the fire department connection (13) Pinhole leaks (14) A 50 percent increase in the time it takes water to travel to the inspector’s test connection from the time the valve trips during a full flow trip test of a dry pipe sprinkler system when compared to the original system acceptance test Semi-Annual: • Commercial Range Hoods are to be inspected by a certified technician twice (2) per year. This inspection includes the replacement of fusible links. • Additional Inspection: Commercial Range Hoods are to be Hydro-tested by a certified technician every twelve (12) years. • Please keep in mind that not all of our sites have a commercial range hood. | [19 empty] | bn
Housing Projects Managed by HRDE—Fire Alarm/Range Hood/Sprinkler/Extinguisher/ Backflow Preventer/ Fire Suppression Inspections (continued)
Annual: • Fire Alarms are required to be inspected by a certified technician once annually. All Devices – refers to the full system, all common area smoke detectors, pull stations and the main panel. • Every five years – Smoke Detectors are to be sensitivity checked. • Please keep in mind that backup batteries for fire alarms usually last five (5) years. – It is a very good practice for a manager to use a permanent black marker and write the install date of the battery on the battery. Annual: • Extinguishers are required to be inspected by a certified technician once (1) annually. • Extinguishers are to be checked monthly by our staff, the individual is to turn the extinguisher upside down, shake it, and double check the gauge on the front of the extinguisher to guarantee that the arrow is in the green area. If everything appears to be functioning properly, they are to print their initials and date on the back of the tag. • Additional Inspection: Fire Extinguishers are to be serviced by a certified technician every six (6) years. This service includes an empty and refill process of the extinguisher. • Additional Inspection: Fire Extinguishers are to be Hydro-tested by a certified technician every twelve (12) years. Annual: • Backflow Preventers are required to be inspected by a certified technician once (1) annually. Each site manager is required to maintain this form in a file onsite.
Housing Projects Managed by HRDE—Fire Alarm/Range Hood/Sprinkler/Extinguisher/ Backflow Preventer/ Fire Suppression Inspections:
Year: |  | Sprinkler: | [7 empty] | (Commercial) Range Hood: |  |  |  | Fire Alarm: |  | Extinguishers: |  | Backflow Preventer:
| Contracted with: | Q1 |  | Q2 |  | Q3 |  | Q4 |  | Semi-Annual |  | Semi-Annual |  | Annual |  | Annual |  | Annual
|  | Date | Cost | Date | Cost | Date | Cost | Date | Cost | Date | Cost | Date | Cost | Date | Cost | Date | Cost | Date | Cost
BPA
CHU
CLU
EUA
FHU
GUA
HRDE MAIN
HVU
LUA
MUA
MUM
RUA
RVA
SCU
SPUP
TPMU
UCA
UHA
WHA
WPA
WUA